## Slide 1
EPICS – Advanced Topics
Edmund Blomley
3.12.2025

## Slide 2: Outline
Part I: Record files
Part II: Data flow and control logic
Part III: Communication with hardware
Part IV: IOC Structure

## Slide 3: Database Record Files
Core component of an IOC
Template file containing multiple database records
Macros/variables $(MACRO_NAME) which will be replaced
P=A:SR:TM:,D=01,val=4
A:SR:TM:01:Out
A:SR:TM:01:In
A:SR:TM:01:Status
P=A:SR:TM:,D=02,val=989
A:SR:TM:02:Out
A:SR:TM:02:In
A:SR:TM:02:Status
P=A:BO:TM:,D=01,val=1
A:BO:TM:01:Out
A:BO:TM:01:In
A:BO:TM:01:Status

## Slide 4: Macro Replacement on IOC Startup
Can be adjusted without rebuilding
Common use case:
  device prefix
  hardware connection handlers
dbLoadRecord()
  Single load of one .db file
source_meter.db
startup file

## Slide 5: Another Example

## Slide 6: IOC Startup with Substitutions file
Replacement of the same .db file many times: substitutions file
dbLoadTemplate(„FILENAME.substitutions");
Global replacements
db file pattern replacements
Replacing multiple .db files

## Slide 7: Advanced Macro Substitions
Default values will used if macro is not replaced: $(MACRO=default)
Lower level replacement
  Requires build / Makefile
  .db file does not exist
Multi-level:
  Not replace prefix during Make

## Slide 8
Data flow and control logic

## Slide 9: Record Processing
One IOC usually has many records
  When are these records „processed“?
  In which order?
Record
Hardware
field(SCAN, „1 second“)
Send to record
Record
Option 1: Regular intervals
  pv.SCAN – options: .1, .2, .5, 1, 2, 5, 10 seconds interval
  Default: passive
Option 2: Triggered / on demand
  By user
  Writing on pv.PROC field
  Other records

## Slide 10: Record Information Exchange
How do records exchange data / information?
Option 1: Record requests data - input
Hardware
field(INP, „@GET_DATA“)
Record
Record
field(OUT, „PV“)
Many record types are either INPUT or OUTPUT records
Some records can also collect/send from/to multiple sources
Important distinction between processing and sending/recieving data
  Exchange data without processing
  Force processing without data exchange
  Trigger processing by data exchange
Option 2: Record sends data – output

## Slide 11: Database Links
Certain fields are links (to other PVs, fields or hardware)
Most links can also be constant values
Links to hardware usually start with @
Link fields:
  INP – input to get data
  OUT – output to send data
  LNK – link for general purposes
  FLNK – forward link to trigger processing
  DOL – desired output location, input link without hardware support

## Slide 12: Record Types
„Variables“ (can also talk to hardware)
bo/bi – binary: boolean
ao/ai – analog: double
longout/longin: integer
stringout/stringin: string
waveform: array
„Functions“
fanout
sequence
calculation
subroutine
In this context the relevant record types can be seen in terms of programming as:

## Slide 13: Fanout Record
Trigger processing of up to 6 records
Usage example: switching on multiple power supplies
record(fanout, PS:Cmd:AllOn)
{
field(LNK1, „PS1:Cmd:On“)
field(LNK2, „PS2:Cmd:On“)
…
field(LNK6, „PS6:Cmd:On“)
field(SELM, „All“)
field(SELN, „“)
}
Optional fields: SELM & SELN – trigger only some links
SCAN also possible
Fanout can trigger other fanouts
LNK = Link
PV of the record to process

## Slide 14: Data Fanout Record
Send data to 8 records (on default no processing)
record(dfanout, PS:Cmd:Output)
{
field(DOL, „PS:Bool“)
field(OUTA, „PS1:Cmd:Output“)
field(OUTB, „PS2:Cmd:Output PP“)
…
field(OUTH, „PS6:Cmd:Output“)
field(SELM, „All“)
field(SELN, „“)
}
DOL: Desired Output Location – input parameter
  PV to read from (example: on/off toggle)
  Constant value
Forces processing after sending the value
Output

## Slide 15: Data Fanout Example
Send data to 40 BPMs, 10 per sector
Full record file – being called for each sector
$(PARAM) provides support for different BPM settings
Use cases: send settings, trigger synchronization…

## Slide 16: Sequence Record
Go through a sequence of 10 steps of getting data from X and sending to Y
record(seq, Sequence:Chain)
{
field(DOL1, „source 1“)
field(LNK1, „target 1“)
field(DLY1, „delay 1“)
…
field(DOL9, „source 9“)
field(LNK9, „target 9“)
field(DLY9, „delay 9“)
field(DOLA, „source 10“)
…
}
DLY: Optional delay of this step by given number in seconds
Use case: actions which have to happen in specific order
Use case 2: As a fanout with varying data per location
Can also be constant

## Slide 17: Sequence Record Example – Booster LLRF
Sequence of commands to get LLRF back to operation after interlock
1
2
3
4
5
6
sequence record

## Slide 18: Sequence Record Example – Booster LLRF
Sequence of commands to get LLRF back to operation after interlock
Only constants
Some delays
Access to fields possible
DISV=0 prevents record from processing
Example for mixture of PVs from different IOCs but same namespace
(full UPPER letters are not allowed in our naming convention, coming from embedded device)
Order of fields irrelevant

## Slide 19: Calc Record
Takes up to 12 input links
Performs calculation
record(calc, Simple:Calc)
{
field(INPA, „source 1“)
field(INPB, „source 2 CP“)
field(INPC, „source 3“)
…
field(INPL, „source 12“)
field(CALC, „Calc Expression“)
}
Forces processing if this source changes
Use case: many! One of the most used record type

## Slide 20: Calc Expression
CALC field also limited to 40 characters
Examples:
  „A + B + 10“
  „(A + B) / 2“
  „MIN(A,B,C,D,E,F)“
Use cases
  Error sums
  Master/slave setups
  Maximum/average vacuum pressure
  …
  …
  …

## Slide 21: Calcout Record & Conditionals
Extends calc record by output location
Relational expressions
Conditional expressions
  „if-statement“
  Syntax: Condition ? True result : false result
  ((A + B) < (C + D)) && G ? !E : F + L + 10

## Slide 22: Calcout Record – Conditional Example
Calcout example with condition and conditional output
  send output only in certain conditions OOPT
    When zero/non-zero („do it as long as…“)
    Transistion To Zero/Non-Zero („do it once“)
„As soon as A gets bigger than B send „5“ once to output location“
record(calcout, Conditional:CalcOut)
{
field(INPA, „source 1“)
field(INPB, „source 2“)
…
field(CALC, „A > B ? 5“)
field(OUT, „out:location“)
field(OOPT, „Transition To Non-zero“)
}

## Slide 23: Example – Beam Lifetime
ai, :LastCurrent
ai, :OldestCurrent
record(calc, :Lifetime) {
field(INPA, „:DiffCurr“)
field(INPB, „:LastCurrent“)
field(INPC, „1“)
field(INPD, „0.0001“)
field(CALC, „(B<C?0:(A<D?0:(60/A*B)))“)
field(FLNK, „:fanout“)
}
A:SR:BeamInfo:01:Current
record(fanout, :fanout) {
field(LNK1, „:hours“)
field(LNK2, „:minutes“)
field(LNK3, „:seconds“)
}
(B < C ? 0
:(A < D ? 0
:(60 / A * B)))
compress, 60s Ring Buffer
calc, :DiffCurr
Zero if current below 1
Zero if current diff is to small
Lifetime is linear slope between
now and 60 seconds ago!

## Slide 24: Subroutine Record
Up to 12 input channels
Executes custom c/c++ functions
record(sub, Subroutine:Record)
{
field(INPA, „source 1“)
field(INPB, „source 2“)
…
field(INPL, „source 12“)
field(SNAM, „name-of-routine“)
}
Advantge: being able to write raw C code
Disadvantage: being able to write raw C code

## Slide 25: How to do more complex things?
Calling any scripts: special module developed by us
  https://gitlab.kit.edu/kit/ibpt/controls/epics/modules/execute
Integrating Python
  Mostly “normal” IOC: pydevsup module to integrate “a bit of Python”
  Mostly Python: Special Python SoftIOC
    IBPT Python Tools module for easy use will be available soon™
More complex and C/C++
  Create your own “EPICS module”
  ASYN: low level async communication with hardware
    Streamdevice: use asyn for text based communication
    areaDetector: use asyn for GigE communication

## Slide 26: Summary Part II: Data flow and control logic
Record processing: External triggers and internal scanning
Data exchange between IOC and IOC/Hardware via links
Record types
  „Variables“: ai, longin, stringin, waveform
  „functions“: fanout, dfanout, calc, calcout, sequence, subroutine
Part III
Communication with hardware

## Slide 27: General Concept
Control system / IOC
Hardware
Interface
RF Generator
Operator
POW?
3
every second
5
5
5

## Slide 28: Device Driver
Record field DTYP (device type) specifies which driver/interface should be used for this record
STREAM
  Streamdevice
  Most used driver at IBPT
  All forms of text based serial communication
    Ethernet/Moxa boxes/USB
    SCPI
AreaDetector
  Many cameras supported out of the box
MOTOR
  Many common motor controller are supported by the EPICS motor modules
  Newport XPSC8 is supported
OPC-UA
  PLC communication
pyDevSup
  Supports interactions with python scripts

## Slide 29: Stream Device
Generic driver for byte stream based communication
  ASCII or binary
  Serial (RS 232, 485)
  IEEE-488 (GPIB)
  TCP/IP
Protocol file defines interpretation of strings

## Slide 30: Stream Device
MEAS:VOL? sent to device
return interpreted as float
written to VAL field of the record

## Slide 31: Stream Device
POW 5.0 is sent to device
VAL is not even used

## Slide 32: Motor Support
Specific driver for certain motor controller
Usually full API is already integrated
Basically one just have to specify how to connect to motor
Includes default GUIs
Newport XPSC8 is supported

## Slide 33: Summary Part III
EPICS supports various methods of communication with hardware
Motors are well supported
PLCs are well supported
Text based communication via streamdevice
  Most used driver at IBPT
  For SCPI one can just use existing protocol files
Part IV
IOC structure

## Slide 34: IOC Envoirnment
Every IOC is an independant C programm
Has to be compiled
EPICS Base and relevant modules (streamdevice, motor support) have to be installed
IBPT envoirnment provides EPICS debian packages
  Custom modifications (like PV length)
  Once installed one can directly build and run IOCs

## Slide 35: IOC File Structure
IOCName/
iocBoot/
common/
st.cmd
iocLinux/
IOCNameApp/
Db/
Makefile
recordFile1.db
recordFile2.db
src/
Makefile
configure/
RELEASE
db/
dbd/
bin/
Compiled folders

## Slide 36: IOC Configuration
IOCName/configure/RELEASE
Define path to EPICS base (version)
Define which modules are used (version)
For modifying IOCs this does not have to be touched
Makes the modules available to the IOC

## Slide 37: IOC Source Folder
IOCName/IOCNameApp/src/
Makefile „loads“ the actual modules and libraries
Only needs adjustments if you need different modules
  If RELEASE is changed
*.dbd defines record structure
  Which fields exist, etc.
_LIBS
  The actual c(++) code

## Slide 38: Database Record Files
IOCName/IOCNameApp/Db/
Place for all database record files
Most used area
Makefile
  Add all .db files
  (autosave) .req files
  (stream) .proto files
  Substitution files

## Slide 39: IOC Start Up Configuration
IOCName/iocBoot/common/st.cmd
Set up network connections
Load .db files
Module specific features
Initialize IOC

## Slide 40: Summary Part IV
EPICS envoirnment
IOC structure
  Configuration of modules
  List of database record files
  Start up config (loading records, establishing communication to hardware)

## Slide 41: IBPT Features
IBPT EPICS bundle
  Extended PV name length (change to EPICS base)
  All relevant modules (motor, streamdevice, autosave, etc…)
changePrefix script adjusts IOCName string
  Makes creating IOCs by copying existing IOCs very simple
Autotab completion for PV names
SALT to deploy, build and integrate IOC
  Runs as system.d process in the background
  Easy start and stop routines
SVN repository hosting all IOCs
  Creating IOCs based on closed match saves a lot of time
Documentation and how-to‘s
Archive system
IBPT CSS bundle
  Very easy installation to powerful GUI

## Slide 42
Part IV.2
Example: Create IOC for LASMagLab – Senis Teslameter
Step 1 - Get similar IOC
Step 2 - Build IOC
Step 3 - Establish hardware communication

## Slide 43: Example – Get Similar IOC
Active IBPT or KARA VPN required
https://scm.anka.kit.edu/scm/svn/kara/epics
svn export https://scm.anka.kit.edu/svm/svn/kara/epics/Teslameter/trunk ./SenisTeslameter
scp –r SenisTeslameter XXX:~/applications/epics/apps/
Use changePrefix script to adjust local name
  In $TOP folder: changePrefix OldName NewName
Create start/stop scripts (by copying and adjusting existing scripts)
  ~/.config/systemd/user/ioc-IOCNAME.service
    If this IOC should be started automatically with PC boot create symlin in default.target.wants subfolder
  ~/bin/ioc-IOCNAME

## Slide 44: Example – Build IOC
Adjust configure/RELEASE
  Correct EPICS base version
  Correct module versions
  Adjust modules if other modules are needed
    (Adjust **App/src/Makefile if other modules are loaded)
Adjust **App/Db/Makefile and .db/.proto files for basic tests
Build IOC
  make in top folder
Start IOC
  ./iocBoot/iocLinux/run in top folder

## Slide 45: Example – Connect to Device and Basic Test
Protocol file (**App/Db/*.proto)
  Set basic configuration (line termination etc)
  Create protocol for basic test command
    Usually basic identification string (*IDN) or simple status flag
Database file (**App/Db/*.db)
  Create basic record using the basic test protocol
Use make in $(TOP)
Adjust start up script (iocBoot/iocLinux/st.cmd)
    drvAsynSerialPortConfigure ("PS1","/dev/ttyS1")
    asynSetOption ("PS1", 0, "baud", "9600")
  Load DB file
  Adjust local path for PV export
Run IOC in local terminal ./iocBoot/iocLinux/run for debugging

## Slide 46: Example – Build Database
Create all records which you want to support
  Not every feature of the hardware has to be implemented
For more complex files consider using tools for record file generation
  Epicsdbbuilder from Diamond (python)
  Write python code, which will be executing while building IOC to create .db files
  https://github.com/Araneidae/epicsdbbuilder
Run IOC with „ioc-IOCNAME start|stop|attach|restart“ command